{"text_format":"3","workbook":"xls","n_sheets":7,"sheets":["Db-1(08-5)","Db-2(08-8)","Db-3(08-10)","Db-4(08-3)","Db-5(08-1)","Db-6(08-2)","Dz-1(08-6)"],"not_rendered":{"images":7,"external_links":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Db-1(08-5)","index":0,"n_rows":25,"n_cols":10,"rows_kept":25,"merged":[[0,0,0,9],[2,0,2,9],[3,0,3,1],[3,3,3,5],[3,6,3,9],[4,0,14,0],[4,1,4,2],[4,3,4,4],[4,5,9,5],[4,7,4,9],[5,1,5,2],[5,3,5,4],[5,7,5,9],[6,1,6,2],[6,3,6,4],[6,7,6,8],[7,1,7,2],[7,7,7,8],[8,1,8,2],[8,7,8,8],[9,1,9,2],[9,7,9,8],[10,1,10,2],[10,5,16,5],[11,1,11,2],[12,1,12,2],[13,1,13,2],[14,1,14,2],[14,7,14,8],[15,0,18,0],[15,1,15,2],[15,3,15,4],[15,7,15,8],[16,1,16,2],[16,7,16,9],[17,1,17,2],[17,3,17,4],[17,7,17,9],[18,1,18,2],[18,7,18,9],[19,1,19,9],[20,0,20,1],[20,2,20,9],[21,0,21,1],[21,2,21,3],[21,4,21,5],[21,6,21,9],[22,0,23,1],[22,4,22,5],[22,8,22,9],[23,4,23,5],[23,8,23,9],[24,0,24,1],[24,4,24,5],[24,7,24,9]],"flags":["formulas_cached_only"]}
["差阻式锚索测力计安装考证表"]
[]
["工程名称：酉水酉酬水电站安全监测工程       "]
["测点编号",null,"Dbp-1","锚索测力计安装位置",null,null,"溢流坝段左边墩(①闸墩)"]
["锚索测力计技术参数","出厂编号",null,"08-5",null,"锚索参数","锚索编号","Z12"]
[null,"生产厂家",null,"南京电力自动化设备总厂",null,null,"结构形式","无粘结锚索"]
[null,"型号",null,"MS-500",null,null,"设计吨位",5468,null,"KN"]
[null,"量程",null,"0～5000","KN",null,"锚束根数",31,null,"根"]
[null,"允许超量程范围",null,{"v":0.2,"d":"20%"},"F.S",null,"锚索长度",19.7675,null,"m"]
[null,"最小读数",null,18.293,"KN/0.01%",null,"与水平面夹角",0.972,null,"°"]
[null,"分辨力",null,{"v":0.003,"d":"0.3%"},"F.S","锁定参数","压力表读数",46,null,"Mpa"]
[null,"绝缘电阻",null,"＞50","MΩ",null,"仪器测值Rs",80.18,null,"Ω"]
[null,"初始测值R0",null,{"v":78.2,"d":"78.20"},"Ω",null,"仪器测值Zs",{"v":10060,"d":"10060.0"},null,"0.01%"]
[null,"初始测值Z0",null,10353.6,"0.01%",null,"锁定吨位",5370.8,null,"KN"]
[null,"物理量计算公式",null,"P=f(Z1-Z0)","(KN)",null,"气    温",13,null,"℃"]
["电缆","接长电缆型号",null,"YSZW5×0.75mm2",null,null,"上游水位",0,null,"m"]
[null,"芯线电阻",null,5.3,"Ω/100m",null,"锁定日期","2008-03-23"]
[null,"芯线接法",null,"A:四芯    B:五芯√ "]
[null,"接长电缆长度",null,"约    7"," m  "]
["安装示意图","　　"]
["埋设说明",null," 仪器电缆按设计图标示走线，引入锚块上部监测站。"]
["施工单位",null,"中南勘测设计研究院                              酉酬水电站安全监测项目部",null,"监理单位",null,"中国水利水电建设工程咨询西北公司             酉酬水电站监理部"]
["有关责任人",null,"审查",null,"校核",null,null,"观测"]
[null,null,"安装",null,"填表",null,null,"填表日期","2008-05-26"]
["监理工程师",null,null,"日期",null,null,"监理评定意见","合格 □     不合格 □ "]

{"sheet":"Db-2(08-8)","index":1,"n_rows":25,"n_cols":10,"rows_kept":25,"merged":[[0,0,0,9],[2,0,2,9],[3,0,3,1],[3,3,3,5],[3,6,3,9],[4,0,14,0],[4,1,4,2],[4,3,4,4],[4,5,9,5],[4,7,4,9],[5,1,5,2],[5,3,5,4],[5,7,5,9],[6,1,6,2],[6,3,6,4],[6,7,6,8],[7,1,7,2],[7,7,7,8],[8,1,8,2],[8,7,8,8],[9,1,9,2],[9,7,9,8],[10,1,10,2],[10,5,16,5],[11,1,11,2],[12,1,12,2],[13,1,13,2],[14,1,14,2],[14,7,14,8],[15,0,18,0],[15,1,15,2],[15,3,15,4],[15,7,15,8],[16,1,16,2],[16,7,16,9],[17,1,17,2],[17,3,17,4],[17,7,17,9],[18,1,18,2],[18,7,18,9],[19,1,19,9],[20,0,20,1],[20,2,20,9],[21,0,21,1],[21,2,21,3],[21,4,21,5],[21,6,21,9],[22,0,23,1],[22,4,22,5],[22,8,22,9],[23,4,23,5],[23,8,23,9],[24,0,24,1],[24,4,24,5],[24,7,24,9]],"flags":["formulas_cached_only"]}
["差阻式锚索测力计安装考证表"]
[]
["工程名称：酉水酉酬水电站安全监测工程       "]
["测点编号",null,"Dbp-2","锚索测力计安装位置",null,null,"溢流坝段左边墩(①闸墩)"]
["锚索测力计技术参数","出厂编号",null,"08-8",null,"锚索参数","锚索编号","Z42"]
[null,"生产厂家",null,"南京电力自动化设备总厂",null,null,"结构形式","无粘结锚索"]
[null,"型号",null,"MS-500",null,null,"设计吨位",5468,null,"KN"]
[null,"量程",null,"0～5000","KN",null,"锚束根数",31,null,"根"]
[null,"允许超量程范围",null,{"v":0.2,"d":"20%"},"F.S",null,"锚索长度",15.9713,null,"m"]
[null,"最小读数",null,18.293,"KN/0.01%",null,"与水平面夹角",15.972,null,"°"]
[null,"分辨力",null,{"v":0.003,"d":"0.3%"},"F.S","锁定参数","压力表读数",46,null,"Mpa"]
[null,"绝缘电阻",null,"＞50","MΩ",null,"仪器测值Rs",78.24,null,"Ω"]
[null,"初始测值R0",null,78.22,"Ω",null,"仪器测值Zs",{"v":10118,"d":"10118.0"},null,"0.01%"]
[null,"初始测值Z0",null,10400,"0.01%",null,"锁定吨位",5143,null,"KN"]
[null,"物理量计算公式",null,"P=f(Z1-Z0)","(KN)",null,"气    温",13,null,"℃"]
["电缆","接长电缆型号",null,"YSZW5×0.75mm2",null,null,"上游水位",0,null,"m"]
[null,"芯线电阻",null,5.3,"Ω/100m",null,"锁定日期","2008-03-21"]
[null,"芯线接法",null,"A:四芯    B:五芯√ "]
[null,"接长电缆长度",null,"约    9"," m  "]
["安装示意图","　　"]
["埋设说明",null," 仪器电缆按设计图标示走线，引入锚块上部监测站。"]
["施工单位",null,"中南勘测设计研究院                              酉酬水电站安全监测项目部",null,"监理单位",null,"中国水利水电建设工程咨询西北公司             酉酬水电站监理部"]
["有关责任人",null,"审查",null,"校核",null,null,"观测"]
[null,null,"埋设",null,"填表",null,null,"填表日期","2008-05-26"]
["监理工程师",null,null,"日期",null,null,"监理评定意见","合格 □     不合格 □ "]

{"sheet":"Db-3(08-10)","index":2,"n_rows":25,"n_cols":10,"rows_kept":25,"merged":[[0,0,0,9],[2,0,2,9],[3,0,3,1],[3,3,3,5],[3,6,3,9],[4,0,14,0],[4,1,4,2],[4,3,4,4],[4,5,9,5],[4,7,4,9],[5,1,5,2],[5,3,5,4],[5,7,5,9],[6,1,6,2],[6,3,6,4],[6,7,6,8],[7,1,7,2],[7,7,7,8],[8,1,8,2],[8,7,8,8],[9,1,9,2],[9,7,9,8],[10,1,10,2],[10,5,16,5],[11,1,11,2],[12,1,12,2],[13,1,13,2],[14,1,14,2],[14,7,14,8],[15,0,18,0],[15,1,15,2],[15,3,15,4],[15,7,15,8],[16,1,16,2],[16,7,16,9],[17,1,17,2],[17,3,17,4],[17,7,17,9],[18,1,18,2],[18,7,18,9],[19,1,19,9],[20,0,20,1],[20,2,20,9],[21,0,21,1],[21,2,21,3],[21,4,21,5],[21,6,21,9],[22,0,23,1],[22,4,22,5],[22,8,22,9],[23,4,23,5],[23,8,23,9],[24,0,24,1],[24,4,24,5],[24,7,24,9]],"flags":["formulas_cached_only"]}
["差阻式锚索测力计安装考证表"]
[]
["工程名称：酉水酉酬水电站安全监测工程       "]
["测点编号",null,"Dbp-3","锚索测力计安装位置",null,null,"溢流坝段左边墩(①闸墩)"]
["锚索测力计技术参数","出厂编号",null,"08-10",null,"锚索参数","锚索编号","Z72"]
[null,"生产厂家",null,"南京电力自动化设备总厂",null,null,"结构形式","无粘结锚索"]
[null,"型号",null,"MS-500",null,null,"设计吨位",5468,null,"KN"]
[null,"量程",null,"0～5000","KN",null,"锚束根数",31,null,"根"]
[null,"允许超量程范围",null,{"v":0.2,"d":"20%"},"F.S",null,"锚索长度",19.7675,null,"m"]
[null,"最小读数",null,18.75,"KN/0.01%",null,"与水平面夹角",30.972,null,"°"]
[null,"分辨力",null,{"v":0.003,"d":"0.3%"},"F.S","锁定参数","压力表读数",46,null,"Mpa"]
[null,"绝缘电阻",null,"＞50","MΩ",null,"仪器测值Rs",79,null,"Ω"]
[null,"初始测值R0",null,79.21,"Ω",null,"仪器测值Zs",{"v":10047,"d":"10047.0"},null,"0.01%"]
[null,"初始测值Z0",null,10326.4,"0.01%",null,"锁定吨位",5231,null,"KN"]
[null,"物理量计算公式",null,"P=f(Z1-Z0)","(KN)",null,"气    温",13,null,"℃"]
["电缆","接长电缆型号",null,"YSZW5×0.75mm2",null,null,"上游水位",0,null,"m"]
[null,"芯线电阻",null,5.3,"Ω/100m",null,"锁定日期","2008-03-24"]
[null,"芯线接法",null,"A:四芯    B:五芯√ "]
[null,"接长电缆长度",null,"约    11"," m  "]
["安装示意图","　　"]
["埋设说明",null," 仪器电缆按设计图标示走线，引入锚块上部监测站。"]
["施工单位",null,"中南勘测设计研究院                              酉酬水电站安全监测项目部",null,"监理单位",null,"中国水利水电建设工程咨询西北公司             酉酬水电站监理部"]
["有关责任人",null,"审查",null,"校核",null,null,"观测"]
[null,null,"埋设",null,"填表",null,null,"填表日期","2008-05-26"]
["监理工程师",null,null,"日期",null,null,"监理评定意见","合格 □     不合格 □ "]

{"sheet":"Db-4(08-3)","index":3,"n_rows":25,"n_cols":10,"rows_kept":25,"merged":[[0,0,0,9],[2,0,2,9],[3,0,3,1],[3,3,3,5],[3,6,3,9],[4,0,14,0],[4,1,4,2],[4,3,4,4],[4,5,9,5],[4,7,4,9],[5,1,5,2],[5,3,5,4],[5,7,5,9],[6,1,6,2],[6,3,6,4],[6,7,6,8],[7,1,7,2],[7,7,7,8],[8,1,8,2],[8,7,8,8],[9,1,9,2],[9,7,9,8],[10,1,10,2],[10,5,16,5],[11,1,11,2],[12,1,12,2],[13,1,13,2],[14,1,14,2],[14,7,14,8],[15,0,18,0],[15,1,15,2],[15,3,15,4],[15,7,15,8],[16,1,16,2],[16,7,16,9],[17,1,17,2],[17,3,17,4],[17,7,17,9],[18,1,18,2],[18,7,18,9],[19,1,19,9],[20,0,20,1],[20,2,20,9],[21,0,21,1],[21,2,21,3],[21,4,21,5],[21,6,21,9],[22,0,23,1],[22,4,22,5],[22,8,22,9],[23,4,23,5],[23,8,23,9],[24,0,24,1],[24,4,24,5],[24,7,24,9]],"flags":["formulas_cached_only"]}
["差阻式锚索测力计安装考证表"]
[]
["工程名称：酉水酉酬水电站安全监测工程       "]
["测点编号",null,"Dbp-4","锚索测力计安装位置",null,null,"溢流坝段左边墩(①闸墩)"]
["锚索测力计技术参数","出厂编号",null,"08-3",null,"锚索参数","锚索编号","Z11"]
[null,"生产厂家",null,"南京电力自动化设备总厂",null,null,"结构形式","无粘结锚索"]
[null,"型号",null,"MS-250",null,null,"设计吨位",2650,null,"KN"]
[null,"量程",null,"0～2500","KN",null,"锚束根数",15,null,"根"]
[null,"允许超量程范围",null,{"v":0.2,"d":"20%"},"F.S",null,"锚索长度",19.7675,null,"m"]
[null,"最小读数",null,8.939,"KN/0.01%",null,"与水平面夹角",0.972,null,"°"]
[null,"分辨力",null,{"v":0.003,"d":"0.3%"},"F.S","锁定参数","压力表读数",40.7,null,"Mpa"]
[null,"绝缘电阻",null,"＞50","MΩ",null,"仪器测值Rs",80.26,null,"Ω"]
[null,"初始测值R0",null,78.27,"Ω",null,"仪器测值Zs",{"v":10122,"d":"10122.0"},null,"0.01%"]
[null,"初始测值Z0",null,10427.5,"0.01%",null,"锁定吨位",2730,null,"KN"]
[null,"物理量计算公式",null,"P=f(Z1-Z0)","(KN)",null,"气    温",13,null,"℃"]
["电缆","接长电缆型号",null,"YSZW5×0.75mm2",null,null,"上游水位",0,null,"m"]
[null,"芯线电阻",null,5.3,"Ω/100m",null,"锁定日期","2008-03-23"]
[null,"芯线接法",null,"A:四芯    B:五芯√ "]
[null,"接长电缆长度",null,"约    7"," m  "]
["安装示意图","　　"]
["埋设说明",null," 仪器电缆按设计图标示走线，引入锚块上部监测站。"]
["施工单位",null,"中南勘测设计研究院                              酉酬水电站安全监测项目部",null,"监理单位",null,"中国水利水电建设工程咨询西北公司             酉酬水电站监理部"]
["有关责任人",null,"审查",null,"校核",null,null,"观测"]
[null,null,"埋设",null,"填表",null,null,"填表日期","2008-05-26"]
["监理工程师",null,null,"日期",null,null,"监理评定意见","合格 □     不合格 □ "]

{"sheet":"Db-5(08-1)","index":4,"n_rows":25,"n_cols":10,"rows_kept":25,"merged":[[0,0,0,9],[2,0,2,9],[3,0,3,1],[3,3,3,5],[3,6,3,9],[4,0,14,0],[4,1,4,2],[4,3,4,4],[4,5,9,5],[4,7,4,9],[5,1,5,2],[5,3,5,4],[5,7,5,9],[6,1,6,2],[6,3,6,4],[6,7,6,8],[7,1,7,2],[7,7,7,8],[8,1,8,2],[8,7,8,8],[9,1,9,2],[9,7,9,8],[10,1,10,2],[10,5,16,5],[11,1,11,2],[12,1,12,2],[13,1,13,2],[14,1,14,2],[14,7,14,8],[15,0,18,0],[15,1,15,2],[15,3,15,4],[15,7,15,8],[16,1,16,2],[16,7,16,9],[17,1,17,2],[17,3,17,4],[17,7,17,9],[18,1,18,2],[18,7,18,9],[19,1,19,9],[20,0,20,1],[20,2,20,9],[21,0,21,1],[21,2,21,3],[21,4,21,5],[21,6,21,9],[22,0,23,1],[22,4,22,5],[22,8,22,9],[23,4,23,5],[23,8,23,9],[24,0,24,1],[24,4,24,5],[24,7,24,9]],"flags":["formulas_cached_only"]}
["差阻式锚索测力计安装考证表"]
[]
["工程名称：酉水酉酬水电站安全监测工程       "]
["测点编号",null,"Dbp-5","锚索测力计安装位置",null,null,"溢流坝段左边墩(①闸墩)"]
["锚索测力计技术参数","出厂编号",null,"08-1",null,"锚索参数","锚索编号","Z41"]
[null,"生产厂家",null,"南京电力自动化设备总厂",null,null,"结构形式","无粘结锚索"]
[null,"型号",null,"MS-250",null,null,"设计吨位",2650,null,"KN"]
[null,"量程",null,"0～2500","KN",null,"锚束根数",15,null,"根"]
[null,"允许超量程范围",null,{"v":0.2,"d":"20%"},"F.S",null,"锚索长度",15.9713,null,"m"]
[null,"最小读数",null,8.961,"KN/0.01%",null,"与水平面夹角",15.972,null,"°"]
[null,"分辨力",null,{"v":0.003,"d":"0.3%"},"F.S","锁定参数","压力表读数",40.7,null,"Mpa"]
[null,"绝缘电阻",null,"＞50","MΩ",null,"仪器测值Rs",78.3,null,"Ω"]
[null,"初始测值R0",null,78.31,"Ω",null,"仪器测值Zs",{"v":10224,"d":"10224.0"},null,"0.01%"]
[null,"初始测值Z0",null,10524,"0.01%",null,"锁定吨位",2690,null,"KN"]
[null,"物理量计算公式",null,"P=f(Z1-Z0)","(KN)",null,"气    温",13,null,"℃"]
["电缆","接长电缆型号",null,"YSZW5×0.75mm2",null,null,"上游水位",0,null,"m"]
[null,"芯线电阻",null,5.3,"Ω/100m",null,"锁定日期","2008-03-21"]
[null,"芯线接法",null,"A:四芯    B:五芯√ "]
[null,"接长电缆长度",null,"约    9"," m  "]
["安装示意图","　　"]
["埋设说明",null," 仪器电缆按设计图标示走线，引入锚块上部监测站。"]
["施工单位",null,"中南勘测设计研究院                              酉酬水电站安全监测项目部",null,"监理单位",null,"中国水利水电建设工程咨询西北公司             酉酬水电站监理部"]
["有关责任人",null,"审查",null,"校核",null,null,"观测"]
[null,null,"埋设",null,"填表",null,null,"填表日期","2008-05-26"]
["监理工程师",null,null,"日期",null,null,"监理评定意见","合格 □     不合格 □ "]

{"sheet":"Db-6(08-2)","index":5,"n_rows":25,"n_cols":10,"rows_kept":25,"merged":[[0,0,0,9],[2,0,2,9],[3,0,3,1],[3,3,3,5],[3,6,3,9],[4,0,14,0],[4,1,4,2],[4,3,4,4],[4,5,9,5],[4,7,4,9],[5,1,5,2],[5,3,5,4],[5,7,5,9],[6,1,6,2],[6,3,6,4],[6,7,6,8],[7,1,7,2],[7,7,7,8],[8,1,8,2],[8,7,8,8],[9,1,9,2],[9,7,9,8],[10,1,10,2],[10,5,16,5],[11,1,11,2],[12,1,12,2],[13,1,13,2],[14,1,14,2],[14,7,14,8],[15,0,18,0],[15,1,15,2],[15,3,15,4],[15,7,15,8],[16,1,16,2],[16,7,16,9],[17,1,17,2],[17,3,17,4],[17,7,17,9],[18,1,18,2],[18,7,18,9],[19,1,19,9],[20,0,20,1],[20,2,20,9],[21,0,21,1],[21,2,21,3],[21,4,21,5],[21,6,21,9],[22,0,23,1],[22,4,22,5],[22,8,22,9],[23,4,23,5],[23,8,23,9],[24,0,24,1],[24,4,24,5],[24,7,24,9]],"flags":["formulas_cached_only"]}
["差阻式锚索测力计安装考证表"]
[]
["工程名称：酉水酉酬水电站安全监测工程       "]
["测点编号",null,"Dbp-6","锚索测力计安装位置",null,null,"溢流坝段左边墩(①闸墩)"]
["锚索测力计技术参数","出厂编号",null,"08-2",null,"锚索参数","锚索编号","Z71"]
[null,"生产厂家",null,"南京电力自动化设备总厂",null,null,"结构形式","无粘结锚索"]
[null,"型号",null,"MS-250",null,null,"设计吨位",2650,null,"KN"]
[null,"量程",null,"0～2500","KN",null,"锚束根数",15,null,"根"]
[null,"允许超量程范围",null,{"v":0.2,"d":"20%"},"F.S",null,"锚索长度",19.7675,null,"m"]
[null,"最小读数",null,9.107,"KN/0.01%",null,"与水平面夹角",30.972,null,"°"]
[null,"分辨力",null,{"v":0.003,"d":"0.3%"},"F.S","锁定参数","压力表读数",40.7,null,"Mpa"]
[null,"绝缘电阻",null,"＞50","MΩ",null,"仪器测值Rs",79.14,null,"Ω"]
[null,"初始测值R0",null,77.46,"Ω",null,"仪器测值Zs",{"v":10011,"d":"10011.0"},null,"0.01%"]
[null,"初始测值Z0",null,10311.9,"0.01%",null,"锁定吨位",2740,null,"KN"]
[null,"物理量计算公式",null,"P=f(Z1-Z0)","(KN)",null,"气    温",13,null,"℃"]
["电缆","接长电缆型号",null,"YSZW5×0.75mm2",null,null,"上游水位",0,null,"m"]
[null,"芯线电阻",null,5.3,"Ω/100m",null,"锁定日期","2008-03-24"]
[null,"芯线接法",null,"A:四芯    B:五芯√ "]
[null,"接长电缆长度",null,"约    11"," m  "]
["安装示意图","　　"]
["埋设说明",null," 仪器电缆按设计图标示走线，引入锚块上部监测站。"]
["施工单位",null,"中南勘测设计研究院                              酉酬水电站安全监测项目部",null,"监理单位",null,"中国水利水电建设工程咨询西北公司             酉酬水电站监理部"]
["有关责任人",null,"审查",null,"校核",null,null,"观测"]
[null,null,"埋设",null,"填表",null,null,"填表日期","2008-05-26"]
["监理工程师",null,null,"日期",null,null,"监理评定意见","合格 □     不合格 □ "]

{"sheet":"Dz-1(08-6)","index":6,"n_rows":25,"n_cols":10,"rows_kept":25,"merged":[[0,0,0,9],[2,0,2,9],[3,0,3,1],[3,3,3,5],[3,6,3,9],[4,0,14,0],[4,1,4,2],[4,3,4,4],[4,5,9,5],[4,7,4,9],[5,1,5,2],[5,3,5,4],[5,7,5,9],[6,1,6,2],[6,3,6,4],[6,7,6,8],[7,1,7,2],[7,7,7,8],[8,1,8,2],[8,7,8,8],[9,1,9,2],[9,7,9,8],[10,1,10,2],[10,5,16,5],[11,1,11,2],[12,1,12,2],[13,1,13,2],[14,1,14,2],[14,7,14,8],[15,0,18,0],[15,1,15,2],[15,3,15,4],[15,7,15,8],[16,1,16,2],[16,7,16,9],[17,1,17,2],[17,3,17,4],[17,7,17,9],[18,1,18,2],[18,7,18,9],[19,1,19,9],[20,0,20,1],[20,2,20,9],[21,0,21,1],[21,2,21,3],[21,4,21,5],[21,6,21,9],[22,0,23,1],[22,4,22,5],[22,8,22,9],[23,4,23,5],[23,8,23,9],[24,0,24,1],[24,4,24,5],[24,7,24,9]],"flags":["formulas_cached_only"]}
["差阻式锚索测力计安装考证表"]
[]
["工程名称：水电站安全监测工程       "]
["测点编号",null,"Dzp-1","锚索测力计安装位置",null,null,"溢流坝段中墩(②闸墩)"]
["锚索测力计技术参数","出厂编号",null,"08-6",null,"锚索参数","锚索编号","Z12"]
[null,"生产厂家",{"$nulls":4},"结构形式","无粘结锚索"]
[null,"型号",null,"MS-500",null,null,"设计吨位",5468,null,"KN"]
[null,"量程",null,"0～5000","KN",null,"锚束根数",31,null,"根"]
[null,"允许超量程范围",null,{"v":0.2,"d":"20%"},"F.S",null,"锚索长度",19.7675,null,"m"]
[null,"最小读数",null,17.595,"KN/0.01%",null,"与水平面夹角",0.972,null,"°"]
[null,"分辨力",null,{"v":0.003,"d":"0.3%"},"F.S","锁定参数","压力表读数",46,null,"Mpa"]
[null,"绝缘电阻",null,"＞50","MΩ",null,"仪器测值Rs",80.4,null,"Ω"]
[null,"初始测值R0",null,78.34,"Ω",null,"仪器测值Zs",{"v":10115,"d":"10115.0"},null,"0.01%"]
[null,"初始测值Z0",null,10412,"0.01%",null,"锁定吨位",5233,null,"KN"]
[null,"物理量计算公式",null,"P=f(Z1-Z0)","(KN)",null,"气    温",20,null,"℃"]
["电缆","接长电缆型号",null,"YSZW5×0.75mm2",null,null,"上游水位",0,null,"m"]
[null,"芯线电阻",null,5.3,"Ω/100m",null,"锁定日期","2008-04-27"]
[null,"芯线接法",null,"A:四芯    B:五芯√ "]
[null,"接长电缆长度",null,"约    25"," m  "]
["安装示意图","　　"]
["埋设说明",null," 仪器电缆按设计图标示走线，引入锚块上部监测站。"]
["施工单位",{"$nulls":3},"监理单位"]
["有关责任人",null,"审查",null,"校核",null,null,"观测"]
[null,null,"埋设",null,"填表",null,null,"填表日期","2008-05-26"]
["监理工程师",null,null,"日期",null,null,"监理评定意见","合格 □     不合格 □ "]